## Лист1
Summary |  |  | Detail
Range | Type | Function | Reg. Address | Description
0-31 | all | reserved | 32 | Analog input 0
32-63 | Input | Analog inputs | 33 | Analog input 1
64-95 | Input | Counters | … | …
96-127 | Input | Digital inputs | 42 | Analog Input 10
128-159 | Holding | Analog outputs | 64, 65 | Counter 0
160-191 | Holding | Digital outputs | 66, 67 | Counter 1
192-223 | Input | System stats | … | …
300-399 | Input + Holding | temperature control | 92, 93 | Counter 14
400-499 | Input | 1-wire raw data | 96 | Digital Inputs
|  |  | 128 | Analog Output 0
|  |  | 129 | Analog Output 1
|  |  | 130 | Analog Output 2
|  |  | 131 | Analog Output 3
|  |  | 160 | Digital Outputs (Read/Write)
|  |  | 161 | Digital Outputs (Set)*
|  |  | 162 | Digital Outputs (Clear)*
|  |  | 163 | Digital Outputs (Toggle)*
|  |  | 192, 193 | System uptime
* - write only
registers (x2bytes)
|  |  | 300 | Channel1 Sensor1 ID | 4 | read/write
|  |  | 304 | Channel1 Sensor2 ID | 4 | read/write
|  |  | 308 | Channel1 Temp Sensor1 | 1 | read/write
|  |  | 309 | Channel1 Temp Sensor2 | 1 | read/write
|  |  | 310 | Channel1 status | 1 | read | b0: channel on/off, b1: sensor1 on/off, b2: sensor2 on/off
|  |  | 311 | Channel1 Current Temp Sensor1 | 1 | read
|  |  | 312 | Channel1 Current Temp Sensor2 | 1 | read
|  |  | 313 | Channel2 | 13
|  |  | 326 | Channel3 | 13
|  |  | 339 | Channel4 | 13
|  |  | 400 | Sensor1 ID | 4 | read
|  |  | 404 | Temperature | 1 | read | 0xffff - invalid. Value * 100
|  |  | 405 | Humidity | 1 | read | 0xffff - invalid. Value * 100
….
|  |  | 190-196 | sensor16 | 6