## Лист1
Summary |  |  | Detail
Range | Type | Function | Reg. Address | Description
0-31 | all | reserved | 32 | Analog input 0
32-63 | Input | Analog inputs | 33 | Analog input 1
64-95 | Input | Counters | … | …
96-127 | Input | Digital inputs | 42 | Analog Input 10
128-159 | Holding | Analog outputs | 64, 65 | Counter 0
160-191 | Holding | Digital outputs | 66, 67 | Counter 1
192-223 | Input | System stats | … | …
250-260 | Holding | System setup | 92, 93 | Counter 14
300-339 | Holding/Input | temperature control setup | 96 | Digital Inputs
350-361 | Input | temperature control status | 128 | Analog Output 0
400-499 | Input | 1-wire raw data | 129 | Analog Output 1
|  |  | 130 | Analog Output 2
|  |  | 131 | Analog Output 3
|  |  | 160 | Digital Outputs (Read/Write)
|  |  | 161 | Digital Outputs (Set)*
|  |  | 162 | Digital Outputs (Clear)*
|  |  | 163 | Digital Outputs (Toggle)*
|  |  | 192, 193 | System uptime
|  |  | 250 | Modbus ID
|  |  | 251 | Settings | bit0: executor bit1: one wire bit2: temperature controller
* - write only
1-Wire and temperature control registers
registers (x2bytes)
channel status bits: |  |  | 300 | Channel1 Sensor1 ID | 4 | read/write
0 | temperature 1 (short loop) OK |  | 304 | Channel1 Sensor2 ID | 4 | read/write
1 | temperature 2 (long loop) OK |  | 308 | Channel1 Temp Sensor1 | 1 | read/write | 0xffff - invalid. (Value + 100) * 100
2 | channel setup t1 OK |  | 309 | Channel1 Temp Sensor2 | 1 | read/write | 0xffff - invalid. (Value + 100) * 100
3 | channel setup t2 OK |  | 310 | Channel2 | 10
4 | safety check error. Heating off |  | 320 | Channel3 | 10
5 | long loop control needs heating |  | 330 | Channel4 | 10
6 | short loop control needs heating
7 | long loop is overheated |  | 340 | Channels control | 1 | read/write
8 | short loop is overheated
9 | control result. 1 = heating |  | 350 | Channel1 status | 1 | read | look at channel status bits
|  |  | 351 | Channel1 Current Temp Sensor1 | 1 | read | 0xffff - invalid. (Value + 100) * 100
|  |  | 352 | Channel1 Current Temp Sensor2 | 1 | read | 0xffff - invalid. (Value + 100) * 100
|  |  | 353 | Channel2 | 3
|  |  | 356 | Channel3 | 3
|  |  | 359 | Channel4 | 3
|  |  | 400 | Sensor1 ID | 4 | read
|  |  | 404 | Temperature | 1 | read | 0xffff - invalid. (Value + 100) * 100
|  |  | 405 | Humidity | 1 | read | 0xffff - invalid. (Value + 100) * 100
….
|  |  | 490-496 | sensor16 | 6